## Govenor Frequency Response
5 % Govenor Droop | [6 empty] | Total Rated Capacity (MWs) | Current Generation (MWs)
63
62 | [8 empty] | Droop | Frequency Scheduled | Frequency Actual | Change in Output
61 | [6 empty] | 500 | 450 | 5% | 60 | 59.9 | 16.6667
60
59 | [7 empty] | Change in Output = | MWs / | Droop % * 60 Hz | Frequency Scheduled | Frequency Actual
58 | [6 empty] | 50 |  | 500 | 3 | 60 | 59.9
57
| 0 | 20 | 40 | 60 | 80 | 100 |  |  | (MWs / Hz) * |  | (Freq. Sched. - Freq. Actual)
[9 empty] | 166.6667 |  | 0.1
Percent Output
[8 empty] | Total Generator Output = |  | 466.6667
OutPut = MWs / 5% * 60 HZ * (Fs - Fa)
Guides
1 | Generating units with nameplate ratings of 10 MW or greater should be equipped with governors operational for frequency response
2 | Govenors should, as a minimum be fully responsive to frequency deviations exceeding + 0.036 Hz.
3 | With a Govenor Droop Characteristic of 5%, 5% * 60 Hz = 3 Hz.
Full Load
50 % Load
No Load