## Power and Frequency Calcs
Frequency Deviation for Load Increase
Droop of Units On-Line | 5
Current Frequency HZ | 60
On-Line Generation Capacity | 1000
Amount of Load Added | 50
Frequency Deviation | -0.15
Required SetPoint Change
Desired Frequency Change - HZ | 0.3
On-Line Capacity - MW | 1000
Droop - % | 5
Change in Set-Points - MW | 100
Generation Surplus
Frequency Deviation - HZ | -0.5
On-Line Capacity - MW | 1000
Droop - % | 5
Generation Surplus - MW | -166.6667